- SECTION 27 05 37

- FIRESTOPPING, SMOKE & ACOUSTICAL SEALING FOR COMMUNICATIONS SYSTEMS

- PART 1 - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division-1 Specification Section, apply to work specified in this section.

1.02	DEFINITIONS

1.03	GENERAL DESCRIPTION OF THE WORK OF THIS SECTION

      - Firestopping of Through Penetrations in Fire Rated Assemblies.

- Only tested firestop systems shall be used in specific locations as follows:  Penetrations for the passage of cables, conduit, and other electrical equipment through fire-rated vertical barriers (walls and partitions), horizontal barriers (floor/ceiling assemblies), and vertical service shaft walls and partitions.

      - Smoke and Acoustical Sealing in Non-Rated Assemblies

- Only tested Smoke & Acoustic systems shall be used in specific locations as follow: penetration for the passage of cables, conduits, and other electrical equipment through non fire-rated vertical and horizontal partitions.

  - RELATED WORK OF OTHER SECTIONS

A.	Coordinate work of this section with work of other sections as required to properly execute the work and as necessary to maintain satisfactory progress of the work of other sections, including:

1.	Section 03 30 00 - Cast-In-Place Concrete

2.	Section 04 20 00 - Unit Masonry

3.	Section 07 84 00 - Firestopping

4.	Section 07 90 00 - Joint Sealants

5.	Section 09 20 00 - Plaster and Gypsum Board

6.	Section 13 48 00 - Sound, Vibration and Seismic Control

7.	Section 21 00 00 - Fire Suppression

8.	Section 27 00 00 - Communications

1.05	REFERENCES

- Test Requirements: CAN/ULC-S115-11, "Standard Method of Fire Tests of Through Penetration Fire Stops"

- Underwriters Laboratories of Canada (ULC) of Scarborough runs CAN/ULC-S115-11 under their designation of ULC-S115-11 and publishes the results in their "FIRE RESISTANCE RATINGS DIRECTORY" that is updated annually.

Underwriters Laboratories (UL) of Northbrook, IL runs ASTM E-814 under their designation of UL 1479 and publishes the results in their "FIRE RESISTANCE DIRECTORY" that is updated annually. UL tests that meet the requirements of ULC-S115-M are given a cUL listing and are published by UL in their “Products Certified for Canada (cUL) Directory.

- International Firestop Council Guidelines for Evaluating Firestop Systems Engineering Judgments

- Inspection Requirements:  ASTM E 2174, “Standard Practice for On-site Inspection of Installed Fire Stops.”

- Test Requirements: ASTM E 90, “Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements”

- Test Requirements: ASTM E 2178, “Standard Test Method for Air Permeance of Building Materials”

- Test Requirements: CAN/ULC-S102-M, “Standard Test Method for Surface Burning Characteristics of Building Materials.”

- Test Requirements: ASTM E 2178, “Standard Test Method for Air Permeance of Building Materials”

- All major building codes:  NBC, OBC, BCBC, and ABC.

- National Electric Code

- National Fire Protection Association (NFPA) – NFPA 101: Life Safety Code

- National Fire Protection Association (NFPA) – NFPA 70: National Electrical Code

- ANSI/TIA-1179-2010 “Healthcare Facility Telecommunications Infrastructure Standard”

- ANSI/TIA-EIA-569 “Commercial Building Standard for Pathway’s and Spaces”

(Note to specifier: Retain or delete building codes listed above as applicable)

1.06	QUALITY ASSURANCE

A.	A manufacturer's direct representative (not distributor or agent) to be on-site during initial installation of firestop and sealing systems to train appropriate contractor personnel in proper selection and installation procedures.  This will be done per manufacturer's written recommendations published in their literature and drawing details.

B.	Firestop System installation must meet requirements of CAN/ULC-S115-11 or UL 2079 tested assemblies that provide a fire rating as shown in Section 2.03 Clauses L & M below.

C.	Proposed firestop and sealing materials and methods shall conform to applicable governing codes having local jurisdiction.

D.	Firestop and sealing systems do not reestablish the structural integrity of load bearing partitions/assemblies, or support live loads and traffic.  Installer shall consult the structural engineer prior to penetrating any load bearing assembly.

E.	For those firestop applications that exist for which no ULC or cUL  tested system is available through a manufacturer, a manufacturer's engineering judgment derived from similar ULC or cUL system designs or other tests will be submitted to local authorities having jurisdiction for their review and approval prior to installation.  Engineering judgment drawings must follow requirements set forth by the International Firestop Council.

1.07	SUBMITTALS

A.	Submit Product Data: Manufacturer’s specifications and technical data for each material including the composition and limitations, and manufacturer's installation instructions to comply with Section 01 30 00.

B.	Submit qualified tested firestop system detail for each firestop application on the project.

C.	Manufacturer's engineering judgment identification number and drawing details when no ULC or cUL system is available for an application.  Engineering judgment must include both project name and contractor’s name who will install firestop system as described in drawing.

D.	Submit safety data sheets provided with product delivered to job-site, if required as per OSHA GHS/Hazard Communication Standard.

1.08	INSTALLER QUALIFICATIONS

A.	Engage an experienced Installer who is certified, licensed, or otherwise qualified by the firestopping/sealing manufacturer as having been provided the necessary training to install manufacturer’s products per specified requirements.  A manufacturer’s willingness to sell its firestopping products to the Contractor or to an Installer engaged by the Contractor does not in itself confer qualification on the buyer.

1.09	DELIVERY, STORAGE, AND HANDLING

A.	Deliver materials undamaged in manufacturer's clearly labeled, unopened containers, identified with brand, type, and ULC or cUL label where applicable.

B.	Coordinate delivery of materials with scheduled installation date to allow minimum storage time at job-site.

C.	Store materials under cover and protect from weather and damage in compliance with manufacturer's requirements, including temperature limitations.

D.	Comply with recommended procedures, precautions or remedies described in material safety data sheets as applicable.

E.	Do not use damaged or expired materials.

1.10	PROJECT CONDITIONS

A.	Do not use materials that contain flammable solvents.

- Scheduling:

- Schedule installation of cast-in place firestop devices after completion of floor formwork, metal form deck, or composite deck but before placement of concrete. Schedule installation of drop-in firestop after completion of floor, but before drilling of openings. Schedule installation of Speed Sleeve, Smoke & Acoustic Sleeve as well as Kit and before openings are being made and cables are run.

- Schedule installation of other firestopping and sealing materials after completion of penetrating item installation but prior to covering or concealing of openings.

C.	Verify existing conditions and substrates before starting work.  Correct unsatisfactory conditions before proceeding.

D.	Weather conditions:  Do not proceed with installation of firestop materials when temperatures exceed the manufacturer's recommended limitations for installation printed on product label and product data sheet.

E.	During installation, provide masking and drop cloths to prevent firestopping materials from contaminating any adjacent surfaces.

- PART 2 - PRODUCTS

- 2.01	GENERAL

- Provide firestopping and sealing materials composed of components that are compatible with each other, the substrates forming openings, and the items, if any, penetrating the firestopping under conditions of service and application, as demonstrated by the firestopping manufacturer based on testing and field experience.

- Provide components for each firestopping system that are needed to install fill material.  Use only components specified by the firestopping manufacturer and approved by the qualified testing agency for the designated fire-resistance-rated systems.

- Provide a round enclosed fire-rated cable management device whenever cables penetrate fire rated walls, or where frequent cable moves, adds and changes may occur.  The fire-rated cable management device shall consist of a corrugated steel tube with zinc coating, contain and inner plastic housing, intumescent material rings and tightly twisted inner fabric smoke seal. The intumescent firestopping material shall automatically adjust to the size of the cable bundle and shall permit cables to be added or removed without the need to remove the firestopping material through the adjustment of the flanges and device threads at the ends of each sleeve.  After the installation of the cables, twist the inner fabric smoke seal so that it seals around the cables. The length of the sleeve shall be 12.4 inches. The fire-rated cable management device shall contain integrated intumescent firestop wrap strip materials sufficient to maintain the hourly rating of the barrier being penetrated.  The fire-rated cable management device shall contain a smoke seal fabric membrane or intumescent firestop plugs sufficient to achieve the L-Rating requirements of the barrier type.

- Provide a round enclosed Smoke & Acoustic cable management device whenever cables or cable bundles penetrate non-fire rated construction (e.g. smoke partition) where frequent cables moves, adds and changes may occur.

- Provide non-curing, re-penetrable, intumescent firestop materials around communications cable trays or ladder racks penetrating through a fire rated wall.  The firestop system assembly shall be able accessible and re-installed from one side of the wall.  The firestop material shall allow up to 12” of unreinforced annular space.

- Penetrations in Fire Resistance Rated Walls: Provide firestopping with ratings determined in accordance with ULC or cUL.

  - F-Rating: Not less than the fire-resistance rating of the wall construction being penetrated.

- Penetrations in Horizontal Assemblies: Provide firestopping with ratings determined in accordance with ULC or cUL.

  - F-Rating: Minimum of 1-hour rating, but not less than the fire-resistance rating of the floor construction being penetrated.

  - T-Rating: when penetrant is located outside of a wall cavity, minimum of 1-hour rating, but not less than the fire-resistance rating of the floor construction being penetrated.

Note to specifier: Retain or delete W-rating listed below if horizontal assemblies require water resistance. W-ratings are not required by the 2006 IBC.

  - W-Rating: Class 1 rating in accordance with water leakage test per UL 1479.

- Penetrations in Smoke Barriers: Provide firestopping with ratings determined in accordance with ULC or cUL.

  - L-Rating: Not exceeding 5.0 cfm/sq. ft. of penetration opening at both ambient and elevated temperatures.

- Mold Resistance: Provide penetration firestopping and sealing with mold and mildew resistance rating of 0 as determined by ASTM G21.

- 2.02	ACCEPTABLE MANUFACTURERS

A.	Subject to compliance with through penetration firestop systems listed in the U.L.C Fire Resistance Directory – Volume III or UL Products Certified for Canada (cUL) Directory, provide products of the following manufacturers as identified below:

1.	Hilti (Canada) Corporation, Mississauga, Ontario

1-800-363-4458

https://www.hilti.ca/

2.	Provide products from the above acceptable manufacturer; no substitutions will be accepted. No know equal.

- 2.03	MATERIALS

A.	Use only firestop products that have been ULC or cUL tested for specific fire-rated construction conditions conforming to construction assembly type, penetrating item type, annular space requirements, and fire-rating involved for each separate instance.

B. 	Re-penetrable, round cable management devices for use with new or existing cable bundles penetrating gypsum or masonry walls, the following products are acceptable:

- Hilti Speed Sleeve (CP 653) with integrated smoke seal fabric membrane

- Hilti Smoke and Acoustic Sleeve (CS-SL SA) for non-fire rated construction

- Hilti Firestop Sleeve (CFS-SL SK)

- Hilti Retrofit Sleeve (CFS-SL RK) for use with existing cable bundles

- Hilti Cable Collar (CFS-CC)

- Hilti Gangplate (CFS-SL GP) for use with multiple cable management devices

- Hilti Gangplate Cap (CFS-SL GP CAP) for use at blank openings in gangplate for future penetrations

C. 	Pre-formed, round firestop devices with integrated intumescent strips for use with noncombustible and combustible pipes (closed and open systems), conduit, and/or cable bundles penetrating concrete floors and/or gypsum walls, the following products are acceptable:

- Hilti Cast-In Place Firestop Device (CP 680-P) for use with combustible penetrants

2.	Hilti Cast-In Place Firestop Device (CP 680-M) for use with noncombustible penetrants

3. 	Hilti Speed Sleeve (CP 653) for use with cable penetrations

4.	Hilti Firestop Drop-In Device (CFS-DID) for use with noncombustible and combustible penetrants

D.	Sealants, foams or caulking materials for use with non-combustible items including rigid steel conduit and electrical metallic tubing (EMT), the following products are acceptable:

- Hilti Intumescent Firestop Sealant (FS-ONE MAX)

- Hilti Fire Foam (CP 620)

- Hilti Flexible Firestop Sealant (CP 606)

- Hilti Firestop Silicone Sealant (CFS-S SIL GG)

- Hilti Smoke and Acoustic Sealant (CP 506) for non-fire rated construction

E.	Intumescent sealants, caulking materials for use with combustible items (penetrants consumed by high heat and flame) including PVC jacketed, flexible cable or cable bundles, and plastic pipe, the following products are acceptable:

- Hilti Intumescent Firestop Sealant (FS-ONE MAX)

F. 	Foams, intumescent sealants, or caulking materials for use with flexible cable or cable bundles, the following products are acceptable:

- Hilti Intumescent Firestop Sealant (FS-ONE MAX)

- Hilti Fire Foam (CP 620)

- Hilti Flexible Firestop Sealant (CP 606)

- Hilti Firestop Silicone Sealant (CFS-S SIL GG)

- Hilti Smoke and Acoustic Sealant (CP 506) for non-fire rated construction

G.	Non-curing, re-penetrable intumescent putty or foam materials for use with flexible cable or cable bundles, the following products are acceptable:

- Hilti Firestop Putty Stick (CP 618)

- Hilti Firestop Plug (CFS-PL)

H.         Wall opening protective materials for use with U.L. listed metallic and specified nonmetallic outlet boxes, the following products are acceptable:

- Hilti Firestop Putty Pad (CP 617 or CFS-P PA)

- Hilti Firestop Box Insert

I.	Materials used for large openings and complex penetrations made to accommodate cable trays and bundles, multiple steel and copper pipes, electrical busways in raceways, the following products are acceptable:

- Hilti Firestop Block (CFS-BL)

- Hilti Composite Sheet (CFS-COS)

- Hilti Firestop Mortar (CP 637)

- Hilti Fire Foam (CP 620)

- Hilti Firestop Board (CP 675T)

J.	Non curing, re-penetrable materials used for large openings and complex penetrations made to accommodate cable trays and bundles, multiple steel and copper pipes, electrical busways in raceways, the following products are acceptable:

- Hilti Firestop Block (CFS-BL)

- Hilti Firestop Board (CP 675T)

- For blank openings made in fire-rated wall or floor assemblies, where future penetration of pipes, conduits, or cables is expected, the following products are acceptable:

      - Hilti Firestop Block (CFS-BL)

      - Hilti Firestop Plug (CFS-PL)

- For penetrations through a Fire Separation wall provide a firestop system with a "F" Rating as determined by ULC or cUL  as indicated below:

| Fire Resistance Rating of Separation | Required ULC or cUL “F” Rating of Firestopping Assembly |
| --- | --- |
| 30 minutes | 20 minutes |
| 45 minutes | 45 minutes |
| 1 hour | 45 minutes |
| 1.5 hours | 1 hour |
| 2 hours | 1.5 hours |
| 3 hours | 2 hours |
| 4 hours | 3 hours |

For combustible pipe penetrations through a Fire Separation provide a firestop system with a “F” Rating as determined by ULC or cUL which is equal to the fire resistance rating of the construction being penetrated.

- For penetrations through a Fire Wall or horizontal Fire Separation provide a firestop system with a “FT” Rating as determined by ULC or cUL which is equal to the fire resistance rating of the construction being penetrated.

- PART 3 - EXECUTION

- 3.01	PREPARATION

A.	Verification of Conditions:  Examine areas and conditions under which work is to be performed and identify conditions detrimental to proper or timely completion.

1.	Verify penetrations are properly sized and in suitable condition for application of materials.

2.	Surfaces to which firestop materials will be applied shall be free of dirt, grease, oil, rust, laitance, release agents, water repellents, and any other substances that may affect proper adhesion.

3.	Provide masking and temporary covering to prevent soiling of adjacent surfaces by firestopping and sealing materials.

4.	Comply with manufacturer's recommendations for temperature and humidity conditions before, during and after installation of firestopping/sealing products.

5.	Do not proceed until unsatisfactory conditions have been corrected.

- 3.02	COORDINATION

A.	Coordinate location and proper selection of cast-in-place Firestop and drop-in devices with trade responsible for the work.  Ensure device is installed before placement of concrete (cast-in) or before drilling of holes (drop-in).

- 3.03	INSTALLATION

A.	Regulatory Requirements:  Install firestop materials in accordance with ULC Fire Resistance Directory or UL Products Certified for Canada (cUL) Directory.

B.	Manufacturer's Instructions:  Comply with manufacturer's instructions for installation of through-penetration materials.

1.	Seal all holes or voids made by penetrations to ensure an air and water resistant seal.

2.	Protect materials from damage on surfaces subjected to traffic.

- 3.04	FIELD QUALITY CONTROL

A.	Examine sealed penetration areas to ensure proper installation before concealing or enclosing areas.

- Keep areas of work accessible until inspection by applicable code authorities.

- Inspection of through-penetration firestopping and sealing shall be performed in accordance with ASTM E 2174, “Standard Practice for On-Site Inspection of Installed Fire Stops” or other recognized standard.

- Perform under this section patching and repairing of firestopping caused by cutting or penetrating of existing firestop systems already installed by other trades.

- 3.05	ADJUSTING AND CLEANING

A.	Remove equipment, materials and debris, leaving area in undamaged, clean condition.

B.	Clean all surfaces adjacent to sealed holes and joints to be free of excess firestop materials and soiling as work progresses.

- END OF SECTION